Technicial Specification

Diesel

Generator Set

KD 35 B&M

Description

This Katana® Power Generation commercial generator set is a fully integrated power generation system, providing optimum performance, reliability, and versatility for stationary standby, prime power and continuous duty applications.

Features

Katana® heavy-duty engine - Rugged 4-cycle industrial diesel delivers reliable power, low emissions and fast response to load changes.

Alternator - Low reactance 2/3 pitch windings; low waveform distortion with non- linear loads, fault clearing short-circuits capability, and class H insulation.

Cooling system - The standart integrated kit model radiator system designed and tested for nominal ambient temparatures, simplifres facility design requirements for heat rejected.

Control system – Datakom electronic control is standard equipment and provides total genset system integration, including auto remote start/stop, alarm and status message display.

Canopy Types - Optionally it is possible to make it protective and soundproof against adverse climatic conditions

Warranty and service - Backed by a comprehensive warranty and worldwide aftersales support, 10 years of spare parts supplying.

Stand by Rating (ESP): It is the way that generators operate under variable load at certaintime ıntervals. It can work as a backup power.It is not suitable to work under extreme load.

Prime Rating (PRP): Applicable for supplying power to varying electrical load for unlimited hours. PRP is in accordance with ISO 8528. 10 % overload capability is available for a period of 1 hour within

12-hour perod of operation,in accordance with ISO 3046.

| Genset Model | Engine Model | Prime rating | Stand by rating |  |
| --- | --- | --- | --- | --- |
| KD 35 B&M | 4M06G35/5 | 32 kVA | 35 kVA |  |

www.katana.com.tr

Manufacturer reserves the right to make changes in model, technical specifications, color, equipment and accessories without prior notice.

Generator Set Specifications

| Governor regulation class | ISO 8528 G3 |
| --- | --- |
| Voltage regulation, no load to full load | ± 1% |
| Random voltage variation | ± 1% |
| Frequency regulation | Isochronous |
| Random frequency variation | ± 0.25% |
| EMS compatibility | In compliance with BS 800 and VDE levels G and N |

Engine Specifications

| Engine brand | Baudouin Engine |
| --- | --- |
| Aspiration Type | Natural |
| Engine Rated Speed | 1500 RPM |
| Bore | 89 Mm |
| Stroke | 92 Mm |
| Displacement | 2,3 | L |
| Cylinder block | 4 cylinder,vertical |
| Oil Capacity | 7.1 | L |
| Coolant Capacity for Engine | 5 L |  |
| Starting voltage | 12 V |
| Fuel system | Direct injection |
| Fuel filter | Strata pore fuel filter |
| Air cleaner type | Heavy duty air cleaner |
| Compression ratio | 17:5:1 |
| Cycle | 4 stroke |
| Cooling system | Liquid (water + 50% antifreeze) |
| Governor Type | Electronic |
| Fuel Consumption at 25% of generator set prime output | 2.4 | L/H |
| Fuel Consumption at 50% of generator set prime output | 4,0 | L/H |
| Fuel Consumption at 75% of generator set prime output | 5.7 | L/H |
| Fuel Consumption at 100% of generator set prime output | 7.6 | L/H |

Alternator Specifications

| Alternator brand | Megatron |
| --- | --- |
| Type | Brushless, revolving field |
| Frequency | 50 Hz |
| Winding pitch | 2/3 pitch |
| Number of bearing | Single bearing |
| Protection | IP23 |
| Insulation system | Class H |
| Standard temperature rise | Standart 125ºC ,Stand by 163ºC |
| Exciter type | Self - excitation or other excitation by PMG |
| Phase rotation | A (U), B (V), C (W) |
| Alternator cooling | Direct drive centrifugal blower fan |
| AC waveform total harmonic distortion (THDV) | No load <1.5%. Non distorting balanced linear load <5% |
| Telephone influence factor (TIF) | <50% per NEMA MG1-22.43 |
| Telephone harmonic factor (THF) | <2% |

Generator Set Options

| Engine | Alternator | Base frame | Canopy Types |
| --- | --- | --- | --- |
|  |  |  | Optional super silent |
| Water jacket | H class insulation | Double wall fuel tank |  |
| heater | Exciter voltage regulator |  |  |

| Cooling | Control panel | Warranty |
| --- | --- | --- |
| Antifreeze -25° | Datakom | Global warranty |

3 pole main circuit

breaker

Motorised 4 pole circuit

breaker

Manufacturer reserves the right to make changes in model, technical specifications, color, equipment and accessories without prior notice.

Control system

The new D300 MK2 genset controller is a cost effective modular genset controller ready for internet monitoring through plug-in modules.

Its main advantages are multifunctionality, support for multiple topologies, harmonic analysis and detailed power measurements.

Description

Software features are complete with easy firmware upgra-de through USB port.

The Windows based PC software allows monitoring and programming through USB, RS-485, RS-232, Ethernet and GPRS.

The Rainbow Scada web service allows monitoring and control of an unlimited number of gensets from a single central location

Major features

- Diesel and gas genset support

- 400Hz operation support

- 400 event logs, full snapshot

- All parameters front panel editable

- 3 level configuration password

- 128x64 graphical LCD display

- Downloadable languages

- Waveform display of V & I

- Harmonic analysis of V & I

- 16Amp MCB & GCB outputs

- 8 configurable digital inputs

- 6 configurable digital outputs

- 3 configurable analog inputs

- Both CANBUS-J1939 & MPU

- 3 configurable service alarms

- Multiple automatic exerciser

- Weekly operation schedule

- Dual mutual standby with equal aging of gensets

- Manual “speed fine adjust” on selected ECUs

- Automatic fuel pump control

- Disable protections feature

- Excess power protection

- Reverse power protection

- Overload IDMT protection

- Load shedding, dummy load

- Multiple load management

- Current unbalance protection

- Voltage unbalance protection

- Fuel filling & fuel theft alarms

- Battery back-up real time clock

- Idle speed control

- Battery charge run enabled

- Combat mode support

- Multiple nominal conditions

- Contactor & MCB drive

- 4 quadrant genset power counters

- Mains power counters

- Fuel filling counter

- Fuel consumption counter

- Modem diagnostics display

- Configurable through USB, RS-232 and GPRS

- Free configuration program

- Allows SMS controls

- Ready for central monitoring

- Mobile genset support• Automatic GSM geo-location

- GPS connectivity (RS232)

- Easy USB firmware upgrade

- IP65 rating with optional gasket

Functions

- AMF unit

- ATS unit

- Remote Start Controller

- Manual Start Controller

- Engine Controller

- Remote Display Panel

Communications

- USB Device

- J1939-CANBUS

- Geo-locating through GSM

- Internet Central Monitoring

- SMS Message Sending

- E-mail Sending

- Free Pc Software: RainbowPlus

- Modbus RTU (2400-57600baud)

- Modbus TCP/IP

- HTML

- UDP

Remote monitoring

- Single server supports up to 60’000 devices

- Provides data security, data is sent to only server

- Uses internet-based interactive World map

- Real time display of status of devices are shown on the map, and on side panel

- Hierarchical configuration and clustering

- Remote control of devices

- Supports all Datakom products, which are integrated with DKG 210 gateway

- Supports all devices, which supports Modbus protocol, by integrating DKG 210 gateway

- Data recording, analysis and reporting

- Tablet and smartphone interfaces

D-300 MK2 control operator / display panel

www.katana.com.tr

Manufacturer reserves the right to make changes in model, technical specifications, color, equipment and accessories without prior notice.

Canopy Standart Specifications

• Compact design connection with non-welded nuts and bolts.

• Integrated canopy,generator set,exhaust system fuel tank.

- Body made from steel components treated with polyester powder coating

- Easy access to all service points

- Exhaust system inside canopy

- Large doors on each side

- Control panel viewing window in a lockable access door

- Emergency stop push button mounted on cabin exterior

- Fuel fill and battery can only be reached via lockable access doors.

- Customer options available to meet your applications needs.

- Katana makes its generating sets noise level tests in accordance with directive 2000/14/EC validation of the noise level test has been aproved by the notified body Szutest (CE conformıty assessment body).

Open

Enclosed

|  |  | Dry Weight (Kg) | Lenght (Mm) | Width (Mm) | Height (Mm) | Tank Capacity (L) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Open type | 750 | 1600 | 900 | 1500 | 112 |  |
|  | Canopy | 850 | 2005 | 900 | 1600 | 112 |  |

Certificates

| Katana Generator has Quality | Katana Generator has Occupational |
| --- | --- |
|  | Health and Safety Management Systems |
| Management Systems certificate. |  |
|  | certificate. |
| ISO 9001:2015 |  |
|  | ISO 18001: 2007 |
| Katana Generator has Environmental | This generator set is available with |
| Management System certification. |  |
|  | CE certification. |
| ISO 14001:2015 |  |

Katana Power Products

Katana Güç Ürünleri San. Tic. Ltd. Şti.

Mazoji Bendrija „Techto” +37060089799 +37060263730 Adresas Vilniaus m. Laisvės pr. 60, 6 aukštas { Vilniaus spaudos rūmai EMAIL: nfo@trafotech.lt www.trafotech.lt